Final — Parameter, Method, and Implementation Justification: Recommended Strategy, Bounds, Voltage and Tariffs Under DC Sessions

**Status: complete (2026-10-07). Run unattended on branch semana-7;

nothing committed. This is the last experimental run; the practical part of

the thesis is closed.**

This document follows the usual mechanism. It is a Markdown record rendered

to .docx by scripts/render_docx.py. The decision log is the last-run

section at the top of thesis_docs/overnight_report.md. The baseline was

HEAD dad3f3e with a clean tree (thesis_docs/final_baseline_status.txt).

Unless stated otherwise, everything uses 42-minute DC sessions (an external,

non-Colombian reference), 8 ports and one 100 kW (112.5 kVA) transformer,

50 seeds × 2 days, and n_clusters = 50.

Headline Results Summary

Objective 4 — infrastructure guidelines (final answer).

1. Operate the station with a transformer-aware Round Robin: round-robin

load management whose power budget is the transformer rating.

It keeps every run within 100 kW.

It serves 95.0% of requested energy at the reference demand (AFAP:

97.6%, but it overloads in 97/100 runs).

It costs 10,141 COP/day [7,816, 12,623] of margin in Bogotá (2.8%).

EV2Gym's own RoundRobin is not this strategy: it follows a

median-smoothed setpoint and never reads the transformer limit.

2. Size it in physical units. The 8-port, 100 kW station meets every

criterion up to 47 offered arrivals/day (763 kWh/day). At **57

arrivals/day (911 kWh/day) it needs 10 ports** on the same unit.

3. Voltage. On EV2Gym's node_123 test feeder, AFAP and the

transformer-aware Round Robin stay within ±5% at 1.0–1.6× (0/50 cells

out of band; lowest bus 0.9733 p.u.; weekday only).

4. **The non-causal MPC and oracle are not upper bounds on service under

DC sessions.** They track the same median-smoothed setpoint and leave

48.5% / 39.9% of demand unserved at 1.0×. MPC is infeasible in 37.7% of

its steps.

Objective 5 — replicability (final answer).

The guideline transfers through two inputs:

the station's own arrivals per day;

the operator's Nivel 2 tariff.

Under a flat tariff the ranking is tariff-invariant (Proposition 7.1).

Under DC load profiles, Air-e's 10.03% two-band option no longer changes

the cost of the limit materially (9,230 COP/day two-band against 9,619

flat), and the cost is about 2.8% of margin in all six categoría especial

cities.

No city's demand is mapped onto the axis, because no per-station demand

source exists.

Part 1 — Parameters and Methods

| Parameter / method | Value | Label | Justification | Source |
| --- | --- | --- | --- | --- |
| Recommended arm | Round Robin, transformer-aware (RoundRobinTransformerCapped) | promoted from diagnostic | The thesis's recommendation (round-robin sharing of the rating) implemented with the rating as the budget. It is causal and needs no forecast | 06 S6.7.1 |
| Budget fraction | 0.999 × rating | labelled | 0.1% margin so float rounding cannot register as overload | ev2gym_thesis/heuristics.py |
| Session model | lognormal, mean 42 min, CV 0.5 (bracket 32 / 78) | external reference, not Colombian | Final capacity brief | U.S. DOE (2023); Hardman (2026) |
| Bounds | MPC_TrackingG2V, Optimal_Oracle_Tracking at 1.0/1.3/1.6× | upper bounds on setpoint tracking, non-causal | Both know departure times. The 4-hour timing rule did not fire, so all 50 seeds were used | tracking_mpc.py; tracking_error.py |
| Voltage protocol | node_123, bus 115, weekday, 50 seeds, idle matched per level | closure E2, unchanged | The only shipped feeder in band when idle | scripts/dwell_ieee123_voltage.py |
| Two-band tariffs | closure D2 tariffs, 15-min DC profiles, 1.0× | post-processing | city_tables reused unchanged | scripts/dwell_multicity_dc.py |
| Criteria | satisfaction counting rejected (CI low ≥ 90%); DNS (CI high ≤ 15%); zero overload in every run; ±5% band in every cell | hardest CI side | As in the closure and dwell runs | analyze_last_run.py |

Final target compliance (DC 42 min, 8 ports, 100 kW; n_clusters = 50).

| Level | Arm | Satisfaction > 90%, served | Satisfaction > 90%, counting rejected | ENS_rel < 15% | DNS < 15% | Transformer within rating | Voltage ±5% |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1× | AFAP | met (CI low 99.8%) | met (97.9%, CI low 97.2%) | met (0.0%) | met (2.4%, CI high 3.2%) | not met (97/100 runs overload) | met on node_123 (0/50 cells out of band) |
| 1× | Round Robin (EV2Gym, setpoint) | met (CI low 94.4%) | met (93.0%, CI low 92.2%) | not met (22.9%) | not met (24.8%, CI high 26.8%) | not met (65/100 runs overload) | not evaluated (not rerun on node_123 under DC) |
| 1× | Round Robin, transformer-aware (recommended) | met (CI low 99.1%) | met (97.3%, CI low 96.5%) | met (2.7%) | met (5.0%, CI high 6.1%) | met (0/100 runs overload) | met on node_123 (0/50 cells out of band) |
| 1× | MPC_TrackingG2V (upper bound, non-causal) | not met (CI low 87.7%) | not met (87.2%, CI low 85.8%) | not met (47.3%) | not met (48.5%, CI high 53.1%) | not met (7/100 runs overload, solver tolerance ≤ 0.0001 kWh/day) | not evaluated (not rerun on node_123 under DC) |
| 1× | Optimal_Oracle_Tracking (upper bound, non-causal) | met (CI low 90.8%) | not met (89.5%, CI low 88.7%) | not met (38.4%) | not met (39.9%, CI high 41.9%) | met (0/100 runs overload) | not evaluated (not rerun on node_123 under DC) |
| 1× | Final RL model (out of distribution) | met (CI low 93.7%) | met (92.2%, CI low 91.5%) | not met (26.3%) | not met (28.1%, CI high 29.6%) | not met (81/100 runs overload) | not evaluated (not rerun on node_123 under DC) |
| 1.3× | AFAP | met (CI low 99.8%) | met (94.7%, CI low 93.7%) | met (0.0%) | met (5.5%, CI high 6.5%) | not met (100/100 runs overload) | met on node_123 (0/50 cells out of band) |
| 1.3× | Round Robin (EV2Gym, setpoint) | met (CI low 95.1%) | not met (90.6%, CI low 89.6%) | not met (19.0%) | not met (23.5%, CI high 25.2%) | not met (83/100 runs overload) | not evaluated (not rerun on node_123 under DC) |
| 1.3× | Round Robin, transformer-aware (recommended) | met (CI low 98.9%) | met (93.9%, CI low 92.8%) | met (3.7%) | met (9.0%, CI high 10.2%) | met (0/100 runs overload) | met on node_123 (0/50 cells out of band) |
| 1.3× | MPC_TrackingG2V (upper bound, non-causal) | not met (CI low 86.7%) | not met (83.3%, CI low 81.9%) | not met (51.7%) | not met (54.4%, CI high 58.7%) | not met (7/100 runs overload, solver tolerance ≤ 0.0001 kWh/day) | not evaluated (not rerun on node_123 under DC) |
| 1.3× | Optimal_Oracle_Tracking (upper bound, non-causal) | met (CI low 91.3%) | not met (87.0%, CI low 86.1%) | not met (35.6%) | not met (39.2%, CI high 40.8%) | met (0/100 runs overload) | not evaluated (not rerun on node_123 under DC) |
| 1.3× | Final RL model (out of distribution) | met (CI low 94.0%) | not met (89.4%, CI low 88.4%) | not met (24.8%) | not met (29.0%, CI high 30.4%) | not met (95/100 runs overload) | not evaluated (not rerun on node_123 under DC) |
| 1.6× | AFAP | met (CI low 99.8%) | not met (89.5%, CI low 88.0%) | met (0.0%) | met (10.5%, CI high 11.8%) | not met (100/100 runs overload) | met on node_123 (0/50 cells out of band) |
| 1.6× | Round Robin (EV2Gym, setpoint) | met (CI low 95.8%) | not met (86.1%, CI low 84.8%) | not met (16.6%) | not met (25.3%, CI high 26.9%) | not met (96/100 runs overload) | not evaluated (not rerun on node_123 under DC) |
| 1.6× | Round Robin, transformer-aware (recommended) | met (CI low 98.8%) | not met (88.6%, CI low 87.2%) | met (4.2%) | not met (14.2%, CI high 15.7%) | met (0/100 runs overload) | met on node_123 (0/50 cells out of band) |
| 1.6× | MPC_TrackingG2V (upper bound, non-causal) | not met (CI low 85.8%) | not met (77.8%, CI low 76.2%) | not met (56.0%) | not met (60.6%, CI high 64.6%) | not met (11/100 runs overload, solver tolerance ≤ 0.0001 kWh/day) | not evaluated (not rerun on node_123 under DC) |
| 1.6× | Optimal_Oracle_Tracking (upper bound, non-causal) | met (CI low 91.7%) | not met (82.5%, CI low 81.2%) | not met (34.4%) | not met (41.3%, CI high 42.8%) | met (0/100 runs overload) | not evaluated (not rerun on node_123 under DC) |
| 1.6× | Final RL model (out of distribution) | met (CI low 94.5%) | not met (84.9%, CI low 83.5%) | not met (22.5%) | not met (30.6%, CI high 32.1%) | not met (98/100 runs overload) | not evaluated (not rerun on node_123 under DC) |

The paired comparisons, the voltage table and the tariff table are in

chapters 06 (S6.7.2–S6.7.3) and 07 (S7.11).

Part 2 — Implementation

`ev2gym_thesis/heuristics.py`, `ev2gym_thesis/figures.py` (relabelled)

The display name is now "Round Robin, transformer-aware", and the docstring

states its promotion. The class name is unchanged, so every registry row

stays valid.

`scripts/run_dwell_capacity.py` (extended), `scripts/run_last_worker.cmd` (new)

The bound arms go through run_week7_grid.run_cell with the DC transform

enabled (MPC through evaluate_mpc, the oracle through

evaluate_oracle, with a per-process replay directory). Their notes carry

upper_bound_noncausal=knows_departure_times,tracks_ev2gym_power_setpoint=True.

Plan: configs/dwell/plans/dwell_bounds.json.

Output: 600 rows appended to results/dwell_registry.csv, which now has

23,800 rows.

`scripts/dwell_ieee123_voltage.py` (new)

This is the closure E2 protocol, reused through the closure script's own

functions and constants. The configs are the closure's grid123_sp* YAMLs

plus a DC sidecar. The transformer-aware arm runs through the heuristic row

builder, with the Week 7 voltage capture. There are 450 runs.

`scripts/dwell_multicity_dc.py` (new)

The closure's attach_bands and city_tables are reused unchanged on the

DC rows at 1.0×. The transformer-aware arm is passed in the "RoundRobin"

pairing slot, which is documented.

`scripts/analyze_last_run.py` (new)

It produces:

the bounds against the transformer-aware Round Robin, with paired

cluster-bootstrap differences and MPC's infeasible-step count;

the node_123 voltage table, with a no-feedback check (station energy

equals the non-grid DC rows);

the 6-arm × 3-level final compliance table.

`scripts/make_figures.py` (extended)

New figures: f19_capacity_threshold_dc, f20_port_options_dc and

f25_voltage_dc.

The Dutch-duration f19 and f20 are kept and relabelled "SENSITIVITY".

Visual QA found and fixed three issues:

f19dc picked its legend handle by position, so it duplicated RL and

dropped the 100 kW line;

the f25 axis label was clipped;

the f20dc legend overlapped a marker.

`scripts/export_dwell_results_xlsx.py` (run), `scripts/extend_progress_log.py` (`--section last`)

Every new table has an .xlsx twin produced through

export_formatted_xlsx.

Progress Log section 17 was appended; nothing earlier was modified.

Tests: `ev2gym_thesis/tests/test_dwell.py` (extended)

TestTransformerAwareBudget steps the recommended arm for 10 seeds × 2 days

at 1.6× and asserts, at every step, that the aggregate transformer power

and the station power are ≤ 0.999 × rating. It also asserts that the budget

actually binds (maximum ratio > 0.9), so the pass is not vacuous.

References (APA 7)

Blu Radio. (2026, May 13). *Conductores en Bogotá podrán cargar hasta el 50 % de batería de su carro eléctrico en menos tiempo* (C. Durán, Author). https://www.bluradio.com/motor/conductores-en-boogta-podran-cargar-hasta-el-50-de-bateria-de-su-carro-electrico-en-menos-tiempo-so35

Enel Colombia. (2024, May). *Avances en infraestructura de recarga de vehículos eléctricos.* https://www.enel.com.co/es/historias/archive/2024/05/infraestructura-de-recarga-de-vehiculos-electricos.html

Hardman, S. (2026). Exploring electric vehicle driver activities and expenditure while using DC fast chargers. *Findings.* https://doi.org/10.32866/001c.162484

U.S. Department of Energy, Vehicle Technologies Office. (2023, December 4). *FOTW #1319: EV charging at paid DC fast charging stations average 42 minutes per session* [Fact of the Week]. https://www.energy.gov/cmei/vehicles/articles/fotw-1319-december-4-2023-ev-charging-paid-dc-fast-charging-stations-average